CENTRAL PUBLIC WORKS DEPARTMENT

लोक निर्माण विभाग

Office of the Executive Engineer, Circle I

NOTICE INVITING e-TENDER No. CE/MM/34/2026-27

Name of work: Supply, installation, testing and commissioning of LT electrical distribution system.

Estimated cost put to tender: Rs. 99,81,000/-

Earnest Money Deposit: Rs. 8,74,000/-

Period of completion: 12 months

Last date of submission: 23.10.2026 up to 15:00 hrs

PART A — INSTRUCTIONS TO BIDDERS

1. The bidder shall submit the EMD in the form of online payment or bank guarantee from a scheduled bank.

2. The tender documents may be downloaded from the e-procurement portal of the Government.

3. The bidder must be registered with the Department in the appropriate class.

4. The successful bidder shall furnish a performance guarantee of 5 % of the contract value within 15 days.

SCOPE OF WORK

This specification covers supply, installation, testing and commissioning of lt electrical distribution system complete in all respects.

SITE CONDITIONS

i) The equipment shall be designed for a maximum ambient temperature of 40°C.

ii) Relative humidity at site may reach 95%.

iii) The installation is at an altitude of less than 1000 m above mean sea level.

PART D — MAIN LT PANEL

i) The LT panel shall conform to IS/IEC 61439-1:2020 and IS/IEC 61439-2:2020.

ii) The panel shall be cubicle type, floor mounted, fabricated from CRCA sheet steel of 2 mm thickness.

iii) The rated operational voltage shall be 415V, 3 phase, 4 wire, 50 Hz.

iv) Main busbars shall be of electrolytic grade aluminium rated for 1600 A continuous current.

v) The busbars and panel shall withstand a short circuit current of 50kA for 1 second.

vi) The degree of protection of the panel enclosure shall be IP54.

vii) The switchboard shall have Form 3b internal separation.

viii) Incomers shall be 1600 A, 4 pole, electrically operated air circuit breakers conforming to IS/IEC 60947-2:2003.

ix) Outgoing feeders shall be MCCBs with ultimate breaking capacity of 36kA.

x) Multifunction meters of accuracy class 0.5 shall be provided on each incomer.

GUARANTEED TECHNICAL PARTICULARS — LT PANEL

| Rated voltage | 415V |
| --- | --- |
| Rated current of main busbar | 1600 A |
| Short time current rating | 50kA for 1 s |
| Degree of protection | IP54 |
| Make and type | (to be furnished by the bidder) |

PART E — LT POWER AND CONTROL CABLES

i) Power cables shall be 1.1 kV grade, aluminium conductor, XLPE insulated, armoured and PVC sheathed, conforming to IS 7098 (Part 1):1988.

ii) The main feeder cable shall be 3.5 core 300 sq mm.

iii) The cables shall be suitable for a maximum continuous conductor temperature of 90°C.

iv) Control cables shall be PVC insulated, copper conductor of 2.5 sq mm, 1.1 kV grade, conforming to IS 1554 (Part 1).

v) Conductors shall be stranded, class 2, conforming to IS 8130.

vi) Cables shall be laid in RCC trenches or on perforated cable trays as shown in the drawings. Cable ends shall be terminated using double compression glands and crimped lugs.

vii) Each drum shall be marked with the manufacturer's name, size, voltage grade and year of manufacture.

6 TESTS AND INSPECTION

i) Routine verification of each assembly shall be carried out in accordance with IS/IEC 61439-1.

ii) Type test certificates of the offered panel design from a NABL accredited laboratory shall be submitted.

iii) Routine test certificates of cables shall be furnished with each consignment.

iv) The equipment shall be inspected by the Engineer-in-charge at the manufacturer's works before dispatch.

7 DOCUMENTATION, WARRANTY AND TRAINING

i) The contractor shall submit detailed shop drawings for approval within 21 days of award of work.

ii) Three sets of operation and maintenance manuals shall be handed over on completion.

iii) The complete installation shall be guaranteed against defective design, material and workmanship for a period of 12 months from the date of handing over.

iv) The contractor shall train the Department's operating staff in operation and routine maintenance.

SCHEDULE OF QUANTITIES

| Sl. No. | Description | Unit | Qty |
| --- | --- | --- | --- |
| 1 | Main LT panel as per specification | Set | 1 |
| 2 | Sub-distribution board, 12 way TPN | No. | 8 |
| 3 | 3.5C x 300 sq mm XLPE armoured cable | m | 350 |
| 4 | Cable tray 300 mm wide | m | 120 |

APPROVED MAKES OF MATERIALS

LT panel builder: as per approved list; ACB/MCCB: L&T / Siemens / Schneider / ABB

Cables: Polycab / KEI / Havells / RR Kabel

Note: Quantities are approximate and may vary during execution.

Note: In case of any discrepancy between drawings and specifications, the decision of the Engineer-in-charge shall be final.

Signature of Bidder with seal

Executive Engineer